UTILITIES DEPARTMENT

HURRICANE PREPAREDNESS PLAN

June 2004

STORMWATER – CONSTRUCTION – WATER DISTRIBUTION

WASTEWATER COLLECTION – ADMINISTRATION – PUMPING STATIONS

EAST AND WEST WATER TREATMENT PLANTS

EMERGENCY TELEPHONE NUMBERS DURING AND AFTER AN EMERGENCY

Voice message announcements informing employees and the public of any messages from the City and employees return to work:

742-6445 - Employee Call-in Line

742-6455 - General Public Call-in Line

City Of Boynton Beach Radio Station	1670 AM

TABLE OF CONTENTS

PRE-SEASON CHECK LIST

CONSTRUCTION/STORMWATER, WASTEWATER COLLECTION,  WATER

DISTRIBUTION, PUMPING STATIONS, MAINTENANCE, ADMINISTRATION	5

EQUIPMENT INVENTORY LIST BY DIVISION

CONSTRUCTION/STORMWATER			6

PUMPING STATIONS/WASTEWATER COLLECTION			7

WATER DISTRIBUTION			8

EAST PUBLIC WATER TREATMENT			9

96 HOURS PRIOR TO ARRIVAL

ADMINISTRATION – PLANT OPERATIONS/MAINTENANCE			10

72 HOURS PRIOR TO ARRIVAL

CONSTRUCTION/STORMWATER, WATER DISTRIBUTION,		    11 & 12

WASTEWATER COLLECTION, PUMPING STATIONS, WATER

TREATMENT

HURRICANE WATCH

CONSTRUCTION/STORMWATER, WATER DISTRIBUTION, 		    13 & 14

WASTEWATER COLLECTION, PUMPING STATIONS, WATER

TREATMENT, ADMINISTRATION

HURRICANE WARNING

CONSTRUCTION/STORMWATER, WASTEWATER COLLECTION, WATER

DISTRIBUTION, WATER TREATMENT EAST, ADMINISTRATION          	 		15

12 HOURS PRIOR TO ARRIVAL

CONSTRUCTION/STORMWATER, WASTEWATER COLLECTION,

WATER DISTRIBUTION, MAINTENANCE, PUMPING STATIONS	          		16

DURING THE STORM

ADMINISTRATION, PUMPING STATIONS, WASTEWATER COLLECTION		17

POST STORM

CONSTRUCTION/STORMWATER, WASTEWATER COLLECTION, 		18

WATER DISTRIBUTION, MAINTENANCE

ADMINISTRATION AND PUMPING STATIONS	     	      19 & 20

ELECTRICAL PROBLEMS AND SUPPLIERS			21

EMERGENCY GENERATOR			21

PUMPS			21

IMPORTANT TELEPHONE NUMBERS

MANAGEMENT - ADMINISTRATION STAFF	                                                       22 & 23

MECHANICS, FIELD INSP./LOCATION, PUMPING STATIONS	                          22 & 23

WASTEWATER COLLECTION, WATER DISTRIBUTION	                                    23 & 24

STORMWATER/CONSTRUCTION                                                                           24 & 25

ITEMS TO BE BROUGHT TO A SHELTER		26

EMERGENCY WATER PURIFICATION		27

HURRICANE SUPPLIES AT O/T BUILDING/WAREHOUSE		28

EAST WATER TREATMENT PLANT					29

PRESEASON PREPAREDNESS								30

DUTY ROSTER										31

CHEMICAL INVENTORY									32

FIRST AID AND SUPPLY CLOSET INVENTORY						33

HARDWARE INVENTORY									34

JANITORIAL INVENTORY									35

SPILL CLEAN-UP INVENTORY								36

SEASON READINESS										37

STORM WATCH THROUGH WARNING							38

DURING THE STORM										39

AFTER THE STORM										40

TELEPHONE LIST - EAST WATER TREATMENT PLANT					41

WEST WATER TREATMENT PLANT							52

CREW SCHEDULE										43

PRESEASON CHECK LIST									45

HURRICANE SEASON SUPPLY LIST								46

HURRICANE CREW SUPPLY LIST								47

STORM WATCH/WARNING ISSUED							    48 & 49

DURING/POST HURRICANE								    49 & 50

OPERATIONS PERSONNEL							                 	50

LAB SERVICE PERSONNEL/CHEMICAL SUPPLY						51

ELECTRICAL/ELEVATOR/EMERGENCY GENERATOR

EQUIPMENT PARTS AND SERVICE					         52-54

PRE-SEASON CHECKLIST

CONSTRUCTION, STORMWATER, WASTEWATER COLLECTION, WATER DISTRIBUTION, PUMPING STATIONS, PUBLIC WATER OPERATIONS

1.	Develop Duty Rosters

a.	Generate a memo soliciting volunteers to work on the hurricane crew.

b.	Select employees from the volunteer list, primarily selecting employees based on level of experience, with two alternates on standby.

2.	Update the hurricane procedures.

3.	Check emergency supplies.

4.	Check equipment:

Portable pumps

Portable generators

Portable ventilators

Portable saws

Emergency lighting

- Organize any loose pipe, couplings, or other material stored outdoors for ease in securing them.

- Fill propane tanks for gas grills.

# ADMINISTRATION

1.	Discuss hurricane procedures at safety meetings.

2.	Develop hurricane duty roster.

3.	Locate, assemble and store the hurricane supplies:

a.	Duct tape

b.	Batteries

c.	Flash lights

d.	Refill first aid kits

The above items are necessary for the storage and security of the computers, files and our after storm supplies for immediate staff.

EQUIPMENT INVENTORY LIST BY DIVISION

Utility Construction – John Wylie - ext. 6412 – Tina Smith – ext. 6484

1	¾ Ton 4x4 Pick-Up with 90 Gal. Portable Diesel Fuel Transfer Tank & Pump Veh. #173

1	¾ Ton Pick-Up with Utility Body - Veh. #156

1	¾ Ton Pick-Up with Utility Body - Veh. #110

1	¾ Ton Pick-Up with Utility Body - Veh. #1132

1	Dump Truck (15 yard.) - Veh. #151

1	John Deer Loader - Veh. #8053

1	Caterpillar 322 Excavator #8125

1	Well Point system & Tag Along Trailer #8116

1	Sullivan 210 CFM Air compressor with 60 & 90 lb. air hammer + 100’ air hose

1	Stihl TS 760 small street saw

1	Target EC-11 large street saw

2	Wacker Vibratory Plate Compactors large BPU-3345A / small 1550AW

1	Rescue Winch, Tripod and Harness

2	Gas Detectors

2	Portable Air Blowers Complete with Ventilation Hoses

1	3000-Watt Honda Portable Electric Generator

1	1000-Watt Honda Small Generator for Hand Saws, Tools, Blowers, etc.

2	Stihl TS400 Hand Held Quick Cut Saws

1	SCI 16" Chain Saw (cuts concrete)

1	Portable Soil Pipe Cutter (cuts up to 12" Clay or Cast Iron Pipe)

1	3” Wacker Mud Hog Pump

1	DeWalt Rotary Hammer drill 1½ “

Utility Stormwater – John Wylie - ext. 6412 – Pat Franklin – ext. 6426

1	½ -Ton Chevy Blazer – Veh. #1119

1	¾ -Ton 4x4 Pick-up with 90 Gal. Portable Diesel Fuel Transfer Tank & Pump- Veh. #134

1	¾ -Ton Utility Pick-up - Veh. #126

1	1-Ton Crew Cab Utility Body – Veh. #1131

1	1-Ton Masons Dump – Veh. #152

1	Dump Truck (8 yard.) - Veh. #139

1	Cat 416C Backhoe - Veh. #8104

1	Crescent 8'x20' Tag Along Trailer #8177

2	Tandem Axle Vac-Con Truck - Veh. #182 & #1125

1	Assortment of Inflatable Air Bags - Range 24"-72"

1	Partner Quick Cut Saw

1	Stihl TS 760 Street Saws

2	Stihl TS400 Hand Held Quick Cut Saws

1	Poulan 12” chain saw

1	Rescue Tripod, Winch & Harness

2	Portable Air Blowers Complete with Ventilation Hoses

1	1000 Watt Honda Small Generator for Hand Saws, Tools, Blowers, etc.

1	2” Wacker Centrifugal Trash Pump

1	3” Wacker Centrifugal Trash Pump

1	4” Multiquip MQ-41TDH Centrifugal Trash Pump

2	6” Centrifugal Trash Pumps #8123 & #8124

1	Bomag double drum vibratory roller BW-60-HG

Pumping  Stations / Wastewater Collection - Tony Lombardi – ext. – 6421 - Jim Hart – ext. 6422

5	Portable Emergency Generators: 230/480 volt-3 phase-65 kw

12	Portable Emergency Generators: 230/480 volt-3 phase-80 kw

1	Skid 65 kw

These units are also capable of I phase/230 volt output. All units are equipped with Russell Stohl JPSIO44FR and WS2O44FR plugs

1	Onan McGraw Generator - 155 kw - skid

1	Portable Transfer Pump: low-head transfer or drainage applications, 2500 GPM, equipped with 8" Traco cam lock fittings 60' of 8" suction hose and 200' of low-pressure drainage hose.

2	Portable Bypass Pump: High-head bypass pumping applications, 600-800 GPM, equipped with 6" cam lock connectors, 60' of 6" suction hose and 100, of low pressure drainage hose.

1	1 Ton Welding Truck equipped with oxygen acetylene and arc welding material (with mig available if required)

5	Retrieval Systems

2 A-Frame Emergency Rescue Systems

1 Manhole

2 Cans

2	20" gas powered chain saws

2	Camera Trucks - Veh. #1110 & #1128

1	Vac-Con Truck - Veh. #1122

1	Vac-Con Truck – Veh. #181

1	CAT Backhoe - Veh. #8103

2	Small Light Duty Trailer

1	Street Saw

1	Soil Compactor

1	6" By-pass Pump #8140

1	4000 kw Portable Equipment Generators

1	1000 kw Portable Equipment Generators

3	Tripod Halogen Site Lighting

2	8 hp 3" Centrifugal Pump

4	12" Quick Saw Cuts

2	Gas Blowers 3 ½ hp

2	Electric Blower

4	Metal Detectors

4	APC Locators

3	3,000 Watt Portable Generators

1	Portable Goodwin 12” Bypass Pump

1	Knuckle-Boom Truck (#169), lifting capacity decreases as boom length increases - 6', 27,450 lbs.; 19', 11,200 lbs.; 42', 3,6OO lbs.; 76', 900 lbs. max.

Miscellaneous safety, first aid and emergency equipment and supplies, including air packs fire extinguishers, rope, etc.

Water Distribution – Les Sarkkinen – ext. 6476

2	Generators: 1000 Watt- 120 Volt

2	Generators: 2500 Watt- 120/240 Volt

1	Small Light-Duty Trailer

1	Large Heavy-Duty Trailer

5	Portable Quick-Cut Saws

4	14" Gas-Powered Chain Saws

4	Tapping Machines

1	Street Saw

2	Soil Compactor

1	Cat Backhoe-Loader (#8159)

1	Trencher and Trailer (#8108 & 8109)

1	Air Compressor with Air Hammer (#8037)

3	Flat Bed Dump Truck (#1124,1126,1108)

- Vac-Tron Trailer – Mounted Vacuum (#1126)

1	Small Dump Truck (#1123)

Miscellaneous safety, first aid, and emergency equipment and supplies, (including barricades/cones, traffic signs, metal detectors, etc.)

East Water Treatment Plant - Melvin Pinkney – ext. 6428

1 Bobcat Loader (#8175)

1 Ton pickup Truck #157

¾ ton Dodge #167

Chevy Blazer 4x4 #1118

1	1ton Utility 4x4 with crane #1107

1	12 Yd Dump truck #1105

1	1/2 ton Pick-up Dodge #191

- 1/2 ton Pick-up Chevy #137 (West)

Portable generators for Wells 8065, 8066, 8105, 8111, 8132 – 125 Kw Onan

Miscellaneous safety, first aid and emergency equipment and supplies including light duty vehicles

96 HOURS PRIOR TO ARRIVAL

# ADMINISTRATION

1.	Staff meeting to review hurricane procedures.

2.	Fuel all vehicles including pool vehicles.

3.	Charge all backup batteries for portable radios.

4.	Remind employees to purchase the supplies needed for home so entire staff is available to report to work the 48-24 hours prior to the storm.

5.	The construction inspectors will visit all active utility construction projects and inform the superintendents that at the time of the hurricane warning (48-24 hours), we expect them to secure their sites before they dismiss their crews and that we will be inspecting their sites.  We will also need a phone number of their local representative who has authority to correct problems that may arise during this inspection.

## PLANT OPERATIONS / MAINTENANCE

1.	Review hurricane procedures with staff.

2.	Review supply check sheets.

3.	Re-fuel vehicles.

4.	Re-fuel diesel tanks.

5.	Inspect/secure all generators.

6.	Inspect/secure all pumps and motors at plants.

7.	Inspect/secure ASR Well.

8.	All volunteers staying at the Plants released to secure homes, pack personal supplies, etc.

72 HOURS PRIOR TO ARRIVAL

CONSTRUCTION/STORMWATER, WATER DISTRIBUTION, WASTEWATER COLLECTION & PUMPING STATIONS, AND WATER TREATMENT EAST

1.	Meet with Committee and/or Department Head.

2.	Initiate plans discussed in the meeting.

3.	Inform personnel of the plans and check all emergency contacts for every employee.

4.	Requisition or purchase any supplies not previously obtained or on hand.

5.	Notify Department Head and/or City Manager of any conditions that may prevent or delay the completion of preparations.

ADMINISTRATION

1.	Review "96 Hours Prior to Arrival" procedures for completion.

2.	Be available to assist other divisions.

3.	Review weekend work assignments.

## PUMPING STATIONS

1.	Call Bill Atkins, Purchasing Department at Ext. 6321 and insist upon immediate diesel fuel deliveries.  Be ready with estimated quantities of fuel needed at each station site to top off tank.  Inform Purchasing that the division will be back in contact after the storm for additional fuel deliveries to keep the equipment on-line until electrical power is restored.  UPS Master Inspection Crews will attend fuel deliveries and note quantities in gallons delivered to each site.  This fuel delivery should be coordinated with the Water Treatment Plant if possible.

Master Station #309-1900 N. Seacrest Blvd.

Master Station #316 – 100 yds. east of the intersection of Military Trail and Golf Road on the north side.

Master Station #317 - 1000' east of the intersection of Boynton Beach Blvd. and Winchester Park Blvd. on the north side.

Master Station #319 - southeast corner of the intersection of Lawrence Road and Knollwood Road at Miner Road.

Master Station #356 - 500 ft. east of the intersection of Boynton Beach Blvd. and Federal Hwy.

Master Station #801 - northwest comer of the intersection of Boynton Beach Blvd. and Lawrence Road

2.	Check and fuel generators and pumps.  Store as indicated.

Generator 8049 (50 Kw) - MS 319

Generator 8084 (65 Kw) - MS 356

Generator 8085 (65 KR) - MS 801

Generator 8086 (100 KR) - MS 317

Generator 8087 (100 KR) - MS 316

Generator 8088 (40 KR) - MS 319

Generator 8089 (40 KR) - MS 309

Pump 8051 (6") – Water Distribution

Pump 8052 (8") – Stormwater

Pump 8102 (8” Godwin)

Pump 8526 (8” Godwin)

Welder on Vehicle #114

Pump (12” Godwin)

5 60KW Generators

HURRICANE WATCH

CONSTRUCTION/STORMWATER, WATER DISTRIBUTION, WASTEWATER COLLECTION & PUMPING STATIONS, AND WATER TREATMENT EAST

1.	Inform all personnel of the condition and the status of the hurricane.  REMIND ALL

EMPLOYEES TO MAKE EMERGENCY ARRANGEMENTS FOR THEIR FAMILIES, ESPECIALLY EMPLOYEES WHO WILL BE ON DUTY.

2.	Ensure all required material and equipment is available and ready for use.

a.	Gas and check all vehicles

b.	Check generators

c.	Check all tools and supplies needed

3.	If a weekend or holiday falls during this period, get any special instructions from the City Manager and/or Department Head regarding necessary preparations and personnel to remain on duty or on call.

4.	Secure the compound.

a.	Barricades, PVC pipe, etc. need to be secured.

5.	Prepare the divisions' fuel reserves for transfers to maintain stationary and portable generators.

4-10 gallon Gerry cans of gasoline

6.	Notify Department Head and/or City Manager of any conditions that may prevent or delay the completion of preparations.

7.	Tour all on-going City construction sites.

ADMINISTRATION

1.	ALL staff will report to work dressed appropriately for the removal and storage of all equipment, supplies and files.  If this interval occurs during the weekend, staff will still report to work at their normal working hours.  This possibility will be discussed before dismissal on Friday.

2.	The construction inspectors will visit and inspect all active utility construction sites (excluding "in-house" construction crews).  They will ensure that all materials are secured, all excavations filled, all lanes of traffic opened, all traffic control devices removed, and all tool trailers removed unless secured according to an active building department permit.

- Assigned drivers will drive City vehicles home.  City vehicles will be parked along side of a secure structure away from large trees.  City vehicles will not be parked in garages, carports, or flood areas.  If a secured structure cannot be located, the City vehicle shall be parked along the roadway, away from large trees.

4.	Portable radios and chargers will be assigned to personnel with instruction on

emergency use.

a.	All staff will be informed of radio assignments.

b.	Vehicle mounted radios will be considered in the assignment of the portables.

c.	Outgoing transmissions will be limited to emergency use only to conserve battery life.  Radios will be left on to receive messages for the first 24 hours after the storm and only during the hours from 7:00 am to 5:00 pm thereafter.

d.	Radio communications will likely be disrupted during and after the storm.

5.	Inform employees which radio stations to monitor post storm for information regarding work.

6.	As soon as the above is accomplished staff will be dismissed to their home and families to prepare for the storm (24 hours to landfall).

## PUMPING STATIONS AND WASTEWATER COLLECTION

1.	Inform all personnel of the condition and the status of the hurricane.  Remind all employees to make emergency arrangements, especially employees who will be on duty.

2.	Ensure that all required material and equipment is available and ready for use.

a.	Fuel and check all vehicles and equipment.

b.	Check generators.

c.	Check all tools and supplies needed.

3.	If a weekend or holiday falls during this period, get any special instructions from the City Manager and/or Department Head regarding necessary preparations and personnel to remain on duty or on call.

4.	Secure all master lift stations.

5.	Prepare the division's fuel reserves for transfers to maintain stationary and portable generators.

Fill 4-10 gallon Gerry cans of gasoline and store in containment areas.

6.	Notify Department Head and/or City Manager of any conditions that may prevent or delay the completion of preparations.

7.	Tour all on-going City construction sites.

HURRICANE WARNING

CONSTRUCTION/STORMWATER, WASTEWATER COLLECTION, PUMPING STATIONS, WATER DISTRIBUTION AND WATER TREATMENT EAST

1.	Assure that all vehicles, equipment, supplies and materials noted during Hurricane Watch Phase are properly prepared.

2.	Office staff to make preparations - clear all desks, cover and unplug all electronic equipment

3.	Personnel not required for hurricane duty will be released, provided all of the above preparations have been completed.

Note:	All Department Personnel not on duty will be on call.

4.	Designate the Divisions' portable radios to the personnel on duty.

5.	Notify Department Head and/or City Manager of any conditions that may prevent or delay the completion of preparations.

6.	Fill all open trenches and excavations.

7	Cover all loose PVC pipe and fittings with dirt.

ADMINISTRATION

1.	As soon as the HURRICANE WARNING objectives are accomplished, staff will be dismissed to their home and families to prepare for the storm (24 hours to landfall).

## PUMPING STATIONS AND WASTEWATER COLLECTION

1.	Ensure all vehicles, equipment, supplies and materials noted above are properly prepared.

2.	Office staff will make their preparations - clear all desks, cover and unplug electronic equipment.

3.	Personnel not required for hurricane duty will be released, provided all of the above preparations have been completed.

NOTE:	 All department personnel not on duty will be on call.

4.	Designate this division's portable radios to the personnel on duty.

5.	Notify Department Head and/or City Manager of any conditions that may prevent or delay the completion of preparations.

12 HOURS PRIOR TO ARRIVAL

# CONSTRUCTION/STORMWATER, WASTEWATER COLLECTION, WATER DISTRIBUTION AND WATER TREATMENT EAST

1.	Assemble all emergency personnel equipment and supplies at the East Water Plant.

2.	Park all vehicles not to be used during emergency in a secure location- DO NOT PARK NEAR THE AREA OF THE VACUUM FILTER BUILDING.

3.	Store extra supplies in the plant.

4.	Secure or remove all loose equipment including barricades from utility work sites.

## PUMPING STATIONS AND WASTEWATER COLLECTION

1.	Division supervisors shall verify that all previous procedures have been completed.

2.	All portable radios should be issued to emergency personnel.

3.	City vehicles will be assigned.  These vehicles will be taken home during the hurricane.

118	Tony Lombardi		196	Ernie Roberts

176	Keith Ellis		1114	Rick Smith

144	Rick Walke		186	Mike Taylor

158	John Martin		133	Barry Hall

183	Scott Smith		114	Mike Dazzo

119	Phil Gillig		1101	Jim Hart

1127	Stan Foster		1134	Marvin Razz

4.	All equipment or vehicles remaining at the plant or at an outlying station will be parked, as much as possible, between or adjacent to a well-built structure, in order to attempt to minimize damage.

5.	Emergency communications will be tested between Central dispatch and Water Treatment Plants to insure usability and to iron out any problems.  Also, the R.A.C.E.S. emergency volunteer radio network (ham radios) shall be tested  (was tested in June 2004.)

6.	All personnel shall be released as soon as possible to weather the storm.

DURING THE STORM

# ADMINISTRATION

1.	Coordinate departmental activities with Central E.O.C.

Prepare press releases and updates as requested by Emergency Operations Chief or City Manager.

## PUMPING STATIONS AND WASTEWATER COLLECTION

I.	Hurricane crew stationed at the East Water Treatment Plant will maintain the facility under the direction of the Chief Operator and secure damage as may be possible without risk of personal injury.

2.	The Assistant Supervisor and Mechanic will continue to monitor VTS Scada / Data Flow Telemetry as long as system remains functional.

3.	Maintain communications with Central dispatch by way of hourly check-in or as necessary by phone. Continue to monitor AM/FM and Weather Radio to track progress and severity of storm.

NOTE:	Crews will be responsible for tracking and submitting detailed reports as to overtime worked during this period as is currently the procedure.  Supervisors will resume this once the crisis has passed and additional crews are called in.

POST STORM

CONSTRUCTION/STORMWATER WASTEWATER COLLECTION, PUMPING STATIONS, WATER DISTRIBUTION AND MAINTENANCE

1.	The following employees, who are normally on emergency call, would take their vehicles home. They would report to work as soon as possible after the "All Clear".  Those employees are:

Stan Foster		1127		Tony Lombardi		118

James Hart		1101		Arkansas Graham	125

Ernie Roberts		196		John Martin		158

George Peck		173		Carlton Brown		164

John Wylie		1119		Rick Smith		1114

Keith Ellis		176		Rick Walke		144

Marvin Razz		1134		Scott Smith		183

The above men would be assigned their normal second man on their particular trucks to the specific zones and would check these zones for damage to the utility system after the storms have passed.  Our Heavy Equipment Operator would be assigned to our 6" pump with his normal assistant, to assist the Utility Mechanics/Lift Station division with lift station pump-outs or the Street Department to assist in pumping out flooded areas, as necessary.  All Jet Vactors would be assigned to clearing storm or sanitary sewer blockage as necessary and pumping out flooded pump stations as required.

2.	When all preparations are completed, we will check with the other divisions to see if they need assistance.

3.	Submit written report to the Department Head and/or City Manager of any damage and status of the repair/clean up.

4.	Submit reports on time employees worked, equipment and materials used.

NOTE:	Employees are responsible for initial reports detailing their actions and time involved on forms provided as they are required to do this on Divisions' regular work reports.

ADMINISTRATION

I.	Employees with radios will monitor City radio transmissions for messages regarding reporting back to work.

2.	Employees will attempt to contact all other division members to determine their condition and availability for returning to work.  Communication will be by telephone or City radio.  If all communications are disrupted, the employees shall monitor the assigned commercial radio station for announcements.

3.	As soon as employees have secured their homes and families they should attempt to contact the Utility Department in person or by other form of communication.  Each employee is responsible to contact the department within 24 hours after the all clear to report his condition and availability for work.

4.	Staff crews who are able will assemble at the East Plant at 7:00 a.m. following the all clear, regardless of the day of the week or previously reporting to work, to determine availability for work and work assignments.  Priority will be given to the protection of person, property and family when availability for work is considered.

## LIFT STATIONS AND WASTEWATER COLLECTION

1.	The hurricane crew stationed at the East Water Treatment Plant will assist as may be necessary and appropriate to place the Plant back into operations.

2.	The Pumping Stations staff will report to their immediate Supervisor by phone, radio or in person if communication systems are out of order.

As designated by the Division Supervisor:

3.	Inspect Storm Pump #415 for proper operation.

4.	Master Station Crew shall inspect each Master Station, assess and secure damages as practical and report verbally on condition of each site and its operational status.  Detailed records must be kept of all findings, condition of equipment, personnel time and materials used.  A written report of facility will be prepared later from these records and notes.

It will be the responsibility of these crews to monitor the fuel levels of the emergency power generation equipment and replenish fuel if possible while under generator power.

5.	As the storm floodwaters recede, Can/Submersible inspection crews will begin inspection of Can and Submersible stations, noting flooded cans for priority action.  Power to any flooded Can Stations will be immediately disconnected when situations arc discovered whether or not FPL power is currently available.  Assess and secure damages as practical and report verbally on condition of each site and its operation status.  Detailed records must be kept of all findings, condition of equipment, personnel time and materials used.  A written report of facility will be prepared later from these records and notes.

Special attention must also be given to residents lifting manhole covers to drain flooded areas.  These will be replaced when found, if possible, reported and barricaded if not possible.

NOTE:  Open manholes can cause serious currents and whirlpools in their immediate vicinity and therefore extreme caution must be used in approaching them.

6.	Staff must give 1st priority to assisting the Water Treatment and Wellfield crews if needed, 2nd to Master Stations, 3rd to flooded Can Stations, 4th to restoration of power and emergency pumping at balance of stations.  The decision as to where the generators will be used will be based on where flooding and overflow causes the greatest danger to the public health.

7.	3", 6", and 8" bypass pumps will give 1st priority to the Water Treatment Plant if flooded, 2nd to Master Re-pump Stations if flooded, 3rd to draining flooded Can Stations, 4th to balance of stations. Staff will set up and operate the pumps as required.

8.	Bypass pumps, Master Station generators, and portable generators will be refueled by fuel cans if necessary, drums preferable, and tanker if possible.  Supervisors will attempt to contact Purchasing Department for refueling if possible or has otherwise been arranged.  Only approved pumps will be used for the refueling process.

9.	Provide written report to the Department Head assessing activities, operations and status of all facilities.

Provide details as to damage to equipment and action taken to mitigate problems.

10.	Arrange for transition of personnel to regular scheduling when possible.

11.	When practical, restart the Hydrogen Peroxide Feed System.

12.	Submit reports on employees' time worked, materials, and other cost items.

13.	Arrange for damage assessment team visitation to each site to compile a report for insurance purposes detailing site and equipment damages.  The team will compile the report from the crew's notes and reports as submitted as well as the site visit.

ELECTRICAL PROBLEMS AND SUPPLIERS

Energy Efficient			(561) 832-2881		Bill Scott

FP & L					(561) 697-8000

(800) 554-4375

Consolidated Electric Supply		(561) 276-0362

Graybar Electric Supply			(561) 585-6148

Johnson Yokogawa Corp.		(800) 524-7378		Peter Lewis

Rich Florin

Dan Ackley

Data Flow Systems			(407) 259-5009		Steve Witlock

EMERGENCY GENERATOR

Advanced Generator			(561) 798-4280		Rich Cordis 635-3165 (mobile)

Cummins Southeastern Power		(305) 821-4200

PUMPS

Godwin Pumps				(770) 335-1982		Mike

Florida Bearing (EMU)	  		(305) 345-8447		Eric

E.K. Phelps (FLYGT)			(561) 848-1200		Steve

UTILITIES DEPARTMENT

IMPORTANT TELEPHONE NUMBERS

1.	MANAGEMENT

Name				Vehicle		Home Ph.	Title

Dale Sugerman			1121		582-5355	Assistant City Mgr.

Cell	436-1810

Peter Mazzella			107		683-8376	Deputy Director

Cell	523-7990

Mark Bobich			106		641-9339	Env. & Safety Coord.

Cell	315-7178

John Reynolds			1118		734-2585	Chief Operator Wells &

Cell	313-0968                  Storage

Steve Evans					499-1533	Supv. Lab Services

Cell	523-8590

David Ailstock			102		433-8779	Chief Operator West

Cell	523-6653

John Wylie			1119		585-8163	Supv. S’water/Const.

Cell	523-8593

Tony Lombardi			118		738-0822	Supvr. Sewage/Pumping Sta.

Cell	523-1484

James Hart			196		369-1955	Asst. Supvr. Sewage/Pumping

Cell	523-7910

Les Sarkkinen			103		753-7969	Supervisor, Meter Reading

Cell	758-7738

Waneya Bryant			105		432-2762	Asst. Supvr. Meter Reading

Cell	704-9627

Terrence Rowe			199		547-5030	System Admin.

Cell	523-8676

2.	ADMINISTRATION STAFF

Barbara Conboy					547-4228	Utilities Manager

Cell	523-7912

Paul Fleming			103		848-2951	Senior Project Mgr.

Cell	389-9912

Debbie Lytle					736-3486	Administrative Clerk

Heidi Crilly					965-8259	Administrative Clerk

Melissa Echevarria				586-0538	Administrative Clerk

Dawn Pfiel					547-8357	Administrative Clerk

Pam Welsh					375-9391	Administrative Clerk

Diena Neville					547-5030	Network Administrator

- MECHANICS

Norman Douglas (Electrical)	145		737-6474	Electrician III

Ken Gerecke			184		641-2835	Mechanic II (West)

Bill McLain (Electrical)		177		642-1932	Instrument & Control Tech.

Ron McCrief			168		272-7581	Mechanic II (West)

Michael Osborn			170		967-3244	Mechanic III (East)

Royston Reddick		157		267-8559	Mechanic II (Wells)

Richard Stone			168		736-8740	Mechanic II (West)

Archie Underwood		1107		no phone	Mechanic II (Wells)

4.	FIELD INSPECTIONS/LOCATIONS

Brent Allen			1120		967-4294	Field Inspector

Cell	523-8674

Iain Gayle			164		533-1420	Location Specialist

Cell	523-8495

Ron Taylor			141		732-8110	Location Specialist

Don Harbol			124		439-8763	Location Specialist

5.	PUMPING STATIONS

Nick Dellibovi			1106		585-6515	Maint. Mech. II

Phil Gillig		119			499-8098	Chief Electrician III

Cell	523-8591

Barry Hall		114			642-7575	Welder

John Martin		158			433-8852	Foreman III

Cell	523-7911

Mike Taylor		186		582-0962	Maint. Mech. II

Keith Ellis			176		732-8955	Electrician Sr

Cell	523-7625

Richard Walke		144		965-5909	Mechanic III

Rick Smith		1114			737-0884	Mechanic III

Stanley Foster			176		585-1790	Electrician

Cell	523-7625

Mike Dazzo			114		432-9696	Maintenance Mechanic

Scott Smith			183		732-2373	Maintenance Mechanic

6.	WASTEWATER COLLECTION

Leon White		122			734-8930	Equipment Operator

Marvin Razz		1134			742-3008	Operator

David Glass		181			736-0560	Operator

Earnest Roberts		196			586-3045	Crew Leader Sr

John Wolcott		1110			735-9591	TV Specialist

Frank Inglese	             1110                               389-5674	Asst. TV Specialist

Darren Antonucci	1122			738-7622	Equipment Operator

James Mims		181			369-5380	Equipment Operator Sr

Royston Reddick, Jr	1113			641-9536	Crew Worker Sr

Karey Isom		1113			735-7414	Crew Worker Sr

Russell Eichorst		1128			737-7928	TV Truck Specialist

Greg Orseno	 	1134			735-4797	Crew Worker Sr

Jim Burt		1103			641-3561	Environmental Inspector

- Water Distribution

Rameau Louis		125			385-7423	Crew Worker Sr.

Rodney Newton		127			737-3093	Equipment Operator

Andre Tookes		1133			278-8211	Crew Leader

Thorley D. Johnson	1133			738-5458	Crew Worker Sr.

Melissa Espinoza	1130			541-3414	Crew Worker Sr.

Carlton Brown		164			266-0341	Crew Supervisor Sr.

Arkansas Graham	125			582-8071	Maint. Tech.

Barbara Vickers		127			3693874	Crew Worker Sr.

Larry LePage		138			967-9277	Crew Worker

Linton Black		1130			735-7642	Crew Leader

- Stormwater/Construction

*George Peck		173			736-0594	Crew Supervisor Sr.

cell	523-4045

*Patrick Franklin	182			737-8863	Utility Operator

*Christopher Olson	182			357-8078	Utility Operator

*Andra Jackson		1125			752-5858	Utility Operator

*Jeffrey Anderson	1125			968-7784	Utility Operator

*Tina Smith		112			737-0884	Utility Operator

Greg Orseno		112			735-4797	Pipelayer

*Pablo Sauberer	156			736-1911	Utility Operator

*Paul Latone		156			493-1336	Pipelayer

Ricky Roundtree	152			737-7908	Maintenance Technician

Kalem Mahdi		110			740-7234	Pipelayer

*Diane Niesolowski	126			738-6818	Crew Worker Sr.

Arthur Harmon		126			741-5822	Crew Worker Sr.

*  Experienced personnel will have a take home vehicle for the storm event and when the all clear is given, they will pick up their assigned partner and meet at the East Water Plant for their assignments.

ITEMS TO BE BROUGHT TO ANY SHELTER

1.	Clothes

2.	Sleeping bags, pillows, air mattresses

3.	Medicines and special foods/needs

4.	Flashlights

5.	Radios and extra batteries

6.	Toiletries

7.	Towels

8.	Games, books, simple toys for children

9.	Snacks

10.	Eyeglasses

11.	Paper cups, plates, napkins, and utensils

12.	Laundry soap

EMERGENCY WATER PURIFICATION

The Utilities Department will issue a boil-water order immediately after the storm if the water supply has become contaminated.  This order will remain in effect for at least 72 hours.

During this time use only your pre-stored water for drinking or cooking.  If you did not store sufficient water and must use water from the tap:

I.	Strain the water through a paper towel or several layers of thick cloth to remove dirt before purifying, or let water settle in a container for 24 hours so that solid particles sink to the bottom.

2.	Use one of the following methods to purify the water:

a.	Keep water boiling at a rolling rate for at least 10 minutes.  You can add a bit of salt to improve taste.

b.	Add four water purification tablets per gallon (follow the directions included – these are available at discount or outdoor camping stores).

c.	Add 12 drops of 2% tincture of iodine per gallon of water.

d.	Add 8 drops of bleach (hypochlorite type only) to 1 gallon of water and mix.  Let stand for 30 minutes and check for a slight chlorine smell.  If there is no odor, repeat and let stand for 15 minutes.  NEVER USE BLEACH CONTAINING SOAP OR ANY OTHER ADDITIVES.

After purification, refrigerate if possible to improve the taste.

HURRICANE SEASON SUPPLIES AT OPERATIONS/TECHNICAL BUILDING

ON							           ON

RECOMMENDED		HAND			RECOMMENDED		        HAND

20	Rolls Duct Tape		20			6	Rubber Boots			  6

10	Rolls Electrical Tape	  4			6	Rubber Gloves			  6

20	Rolls Masking Tape	20			4	Safety Belts			  4

12	AAA Batteries		12			12	Safety Vests			12

20	AA Batteries		20			8	Safety Flags			  8

20	C Batteries		20			8	Safety Cones			  8

36	D Batteries		36			2	Rolls Barricade Tape		  2

12	6 Volt Batteries		12			4	Portable Radios AM/FM	  4

12	9 Volt Batteries		12			1	20 pound bag Charcoal		  1

6	Flashlights(D cell)	  6			8	Cots				  8

6	Lantern Lights (6V)	  6			2	Rolls Thin Tie Wire		  2

4	First Aid Kits		  4			2	Cases Fusee Flares		  2

6	Sets Jumper Cables	  6			4	Shovels				  4

800'	⅜" Nylon Rope		800'			6	Bags Plastic Wire Ties		  6

6	Rolls Visqueen		  6			6	Garbage Bags			  6

12	Raincoats		12			12	Cans Silicone Spray		12

6	Cans PVC Cleaner	  6			24	Gallons of D.I. Water	         (Lab)

6	Cans PVC Glue		  6			12	5 Galllon Fuel Cans		12

2	Gallons Bar Oil		  2

SUPPLIES RESERVED FOR UTILITIES AT WAREHOUSE

12	Hard Hats						12	Rain Suits

5	First Aid Kits						10	Blankets

3	5 gal. Water Jugs					18	Flashlights

20	D Batteries						16	6 Volt Batteries

1	Case Paper Plates					  8	Bath Towels

1	Pack Plastic Utensils					  8	Kitchen Towels

3	Bed Pillows						  8	Washcloths

1	Gas Stove & 6 cans propane				  1	Hot Plate (2 burner electric)

3	Fire Extinguishers					  1	100 quart Cooler

1	Camp Set/Pots-Spoons					18	Cans Orange Spray Paint

1	Polaroid Camera (no film)

HURRICANE EMERGENCY PLAN

EAST WATER TREATMENT PLANT

EAST WATER TREATMENT PLANT

PRE-SEASON PREPAREDNESS

This Pre-Season Preparedness section shall be performed and completed before May 31st.

- The Chief Operator will review the Hurricane Procedure and revise or update as required.

- The Chief Operator will review the duty roster with team members and update as necessary.

- Team members will be assigned to inventory - Chemical, First Aid, Hardware, Janitorial, and Spill Cleanup supplies.  Orders will be placed as needed to meet basic required stock as indicated on attached inventory sheets.  (Note: On hand supplies will be increased during this time.  Fire Extinguishers are always checked and sent for service if needed monthly).

- The Chief Operator will inspect plant, accompanying buildings and grounds.  A working list will be assigned to team members for initial cleanup and securing of facilities.

- Team members will be assigned to exercise all hurricane shutters and issue work orders if necessary for repairs.

- After above has been completed: the Revised Hurricane Plan, Duty Roster, Supply Inventory status, and condition of site will be reviewed and discussed at a special team meeting.  Staff will be advised to pay close attention to work areas with emphasis placed on: expediting work orders, checking/replacing burned out light bulbs, and restocking supplies.  Volunteers will be advised to begin assembling non-perishable personal supplies.

- The Chief Operator will update Deputy Director, and all members of the H2O on the Go Team of preparedness status.

- A copy of the revised plan will be sent to Administration for inclusion in Department Plan.

EAST WATER TREATMENT PLANT

DUTY ROSTER

Melvin Pinkney, Chief Operator

Operators

Alan Brock

Melvin Pinkney, Operator III

Thomas P. Fitzgerald, Operator III

Jack Holdam

David Roland

Phill Taylor

Process Technicians

Robert Greene, Process Technician

(Kenneth Calvin, Process Technician-Not Available)

Duran Millines

# Maintenance Mechanic

Rayanthony Mitchell, Utility Mechanic II

Michael Osborn

Items to be brought with you to the plant:

Clothes

Sleeping bags, pillows, air mattresses

Medicine, special foods

Flashlights

Radios and extra batteries

Toiletries

Towels

Games, books

Snacks

Eyeglasses

Paper cups, plates, napkins, utensils

Laundry soap

Perishable and non-perishable foods

CHEMICAL INVENTORY

(Hurricane Preparedness)

Current On Hand			Recommended

Supply				      Supply___

Ammonia: Tank East %								50% full

Psi

Ammonia Tank West %								50% full

Psi

Chlorine Tons:	Full								        5 full

Empty

In Service							5 full on line

Fluoride Tank

Gal.								50% Full

Chlorine Granular HTH:							10-100 lb. Drums

Chlorine Liquid:								3 – 55 gal. drums

Lime Silo:	North								40 Tons

South								40 Tons

Muriatic Acid:									3 - 55 gal. Drums

Phosphate:									30 - 40 lb. Bags

Polymer:									3 - 55 gal. Drums

Sulfamic Acid:									2 - 50 lb. Bags

FIRST AID INVENTORY

(Hurricane Preparedness)

Check each of the following First Aid Kits.  They should have the supplies listed below.  If not, re-stock from supply closet and then do the supply closet inventory.

Kit location:

Control Room: _____  HSP 4: _____  Lunch Room: _____  Chemical Bldg.: _____

Supply Closet Inventory

Current On Hand		Recommended

Supply			     Supply____

Burn Spray (Special Order)								 6 each

Sterile Water (each)									12 each

Hydrogen Peroxide (each)								12 each

Tape ½" (box)										 6 each

Tape 1" (box)										 6 each

2x2 Gauze Pads (bag)									 1 bag

4x4 Sterile Gauze Pads (bag)								 6 boxes

2" Sterile Kling Gauze (box)								 2 boxes

4" Sterile Kling Gauze (box)								 2 boxes

¾"x3" Bandaids (box)									 2 boxes

Alcohol Prep Pads (box)								 2 boxes

Bandage Scissors (each)									 2 each

Cold Packs (case)									 1 dozen

Ammonia Inhalants (each)								 2 each

Benzoin tincture Swabs (box)								 2 boxes

CPR Pocket Mast (each)								 2 each

HARDWARE INVENTORY

(Hurricane Preparedness)

Current On Hand	Recommended

Supply			Supply

Utility Knife (each									2 each

Utility Knife Blades (pk/5)								2 packs

¾" x 50' Garden Hose (each)								2 each

¾" Pistol Grip Hose Nozzle (each)							2 each

2 Cell Flashlight (each)									4 each

"AA" Batteries (each)									6 each

"D" Batteries (each)								           12 each

5 Gallon Water Keg (each)								1 each

4'x8'x2/4 Plywood (each)								2 each

⅜" Nylon Braid Rope (ft)							            50 feet

1 ½" Masking Tape (roll)								4 rolls

2" Masking Tape (roll)									4 rolls

50' Outdoor Extension Cord (each)							1 each

Plastic Sheeting (roll)									3 rolls

JANITORIAL INVENTORY

(Hurricane Preparedness)

Current On Hand		Recommended

Supply			     Supply

Stirrup Grip Mop Handles (each)								6 each

24 oz Cotton Mop Heads (each)								           12 each

Jumbo Roll Towels (cs/12)									3 cases

Jumbo Roll Toilet Tissue (cs/6)									3 cases

Trash Can Liners (cs/200)									2 cases

Black Trash Bags (cs/100)									3 cases

Rags, White Cotton (bx 10 lb)									4 boxes

Rag on Roll (case)										2 cases

Hand Soap Refills (case)									1 case

Dishwashing Liquid (gal)									1 gallon

Laundry Powder (50 lbs.)								           10 lbs.

Scrub Brush (each)										2 each

Bowl Mops (each)										2 each

Sponge w/Scouring Pad (each)									1 dozen

All Purpose Cleaner (each)									4 each

Lysol Cleaner (each)										6 each

Glass Cleaner (each)										4 each

Bleach (gallon)											4 each

Ajax Cleanser (each)										4 each

SPILL CLEANUP INVENTORY

(Hurricane Preparedness)

Current On Hand		Recommended

Supply			     Supply

Absorbent Pads (3 quotes)									1 case

Absorbent Pillows (3 quotes)									1 case

Safe Step (35 lb. Bag)										6 bags

55 Gallon Drum Kit										1 kit

Chlorine Repair Kit										1 kit

SEASON READINESS

Throughout hurricane season the plant will be maintained in an "on guard" status.

- Patrolling and cleanup of grounds will be done twice weekly by non-operating day shift staff.

- Hurricane Preparedness inventories will replace "routine" inventories weekly.

- Tropical weather conditions will be monitored daily by staff on all shifts.

- All vehicles will be fueled when tank levels reach half.

- Generator fuel tank levels are monitored weekly and kept at a minimum of 75% full.

- Storage closets, offices, and hallways will be kept free of clutter.

- Employee, vendor and emergency phone numbers will be updated as needed.

- Staff will be reminded of the need to have non-perishable supplies packed and ready.

EAST WATER TREATMENT PLANT

HURRICANE WATCH THROUGH WARNING

Upon issuance of a hurricane watch to South Florida by the National Weather Service, the following sequence of events will be initiated:

NOTE: If watch comes during normal working hours, Monday through Friday, all plant personnel will be required to assist in securing the main plant, chemical building and vacuum filter building before being released from duty.

- The Chief Operator will advise Deputy Director and West Plant Chief Operator of sequence initiation.

- All hurricane shutters for the main plant will be closed

- All hurricane shutters for the Chemical Building will be closed.

- The Vacuum Filter Building will be secured.

- Diesel fuel tanks at the main plant, wellfield and 3 MG Ground Storage Tank will be filled.

- All vehicles will be fueled and parked in the graveled area north of the East Treatment Basin as close to the Recarbonation Basin as possible.

- Staff will be released to prepare their residences for storm.  If a warning is imminent, take care of family members and supplies.  Return to work ASAP.

- The exterior of hallway windows facing into the Control Room will be covered with plywood for added protection.  Operations will have plywood on hand.

- Plant grounds will be inspected and cleaned up.  All portable non-flammable equipment will be stored in the garage area, janitorial supply room, and if necessary, high service pump room.

- Telephone, radio and computer communications with the West Water Plant will be verified.

- The Chief Operator will advise Deputy Director, Maintenance Supervisor, and West Plant Chief Operator of sequence completion.

ONCE THE WARNING IS ISSUED:

- All chemical feed day tanks will be kept full.

- The elevated storage tank, ground storage tanks and clearwell will be kept as full as practical.

- All portable radio batteries will be brought to the main plant control room and kept charged.

- All communication with the West Water Plant will be by phone to preserve radio batteries.

- After all on duty personnel have arrived, some exterior doors will be locked or roped closed.

- Plant staff will occupy main plant control room and/or chemical building.

- The Chief Operator will advise Deputy Director, and West Plant Chief Operator of readiness.

DURING THE STORM

##### EAST WATER TREATMENT PLANT

The plant will remain fully operational until the Chief Operator determines that weather or other conditions prohibit safe periodic inspections of the chemical building.  If this happens, all chemical feed equipment, with the exception of chlorine, will be shut down.  A free chlorine residual of 3.0 mg/l and a minimum distribution system pressure of 40 psi will be maintained for as long as possible.

The Control Room Operator will check in with the West Water Plant at least hourly by phone until power is lost.  After that, a portable radio will be used sparingly to conserve battery power.

Auxiliary generators may be engaged at the first loss of power.  Generators will be rotated to conserve fuel.

All efforts will be made to keep the plant on line and staff safe; however, should the storm be extremely destructive, the plant will be shut down to preserve life and equipment from further damage and/or risk.

AFTER THE STORM

##### EAST WATER TREATMENT PLANT

As soon as the storm is over and the all clear is issued:

- Plant staff will assist the mechanics and other personnel as necessary in inspection of the facility or other assigned duty.

- The plant will be returned to service as quickly as possible.

- Off duty personnel will be called and required to return to work to assist in operation and cleanup of plant and grounds and/or other assigned duty.

- The Chief Operator will submit a full report of events, damage, employee injury, and overtime to the Deputy Director as quickly as reasonably possible or within 24 hours of plant startup.

TELEPHONE LIST

##### EAST WATER TREATMENT PLANT

STAFF							CITY EXTENSIONS

Alan Brock		561-389-0385			West Plant		6450

Michael Osborn		561-441-2098

Earl Crossman		561-248-3474			John Reynolds		6433

Rayanthony Mitchell	561-379-4331

Robert Greene		561-329-3376			Dale Sugerman		6456

Thomas P. Fitzgerald	561-733-9771

Kenneth Calvin		Not Available

Duron Millines		561-375-8762

Melvin Pinkney		561-586-3983

Gus Gall		561-752-8591

Jack Holdam		561315-5518

David Roland		561-732-2441

Norm Douglas		561-737-6474

John Burns		561-582-4185

Phill Taylor		561-239-4088

Ron McCrief		561-523-6642

SUPPLIERS

Ammonia		Bower Ammonia		1-800-643-6226

Chlorine		Jones Chemicals		1-954-484-3035

Diesel Fuel		B V Oil				1-800-586-2862

Lime			ChemLime			1-800-695-5657

Phosphate		Sweetwater			1-931-540-1334

Polymer		LeaChem Industries		1-321-269-6510

MISCELLANEOUS

Chemical Spills		Chemtrec			1-800-424-9300

Electric Service		Florida Power & Light		1-800-375-2434

Generator Repair	Advanced Generator		561-798-4280

Injury Reporting	Risk Management		742-6677 (OOPS)

##### HURRICANE PROCEDURE

WEST WATER TREATMENT PLANT

LABORATORY SERVICES

WEST WATER TREATMENT PLANT

2004 HURRICANE CREW SCHEDULE

June 2004

CREW	-		Terry Daeumler	, John Richards, Ford Babcock, Richard Stone

Bill McLain

ALTERNATES	Charles Barnes, Pete Villanacci

July 2004

CREW			Terry Daeumler	, John Richards, Charles Barnes, Bill McLain

Pete Villanacci

ALTERNATES	Ford Babcock, Richard Stone

August 2004

CREW			Terry Daeumler	, John Richards, Ford Babcock, Ken Gerecke

Bill McLain

ALTERNATES	Charles Barnes, Pete Villanacci

##### September 2004

CREW-		Terry Daeumler, Ford Babcock, Charles Barnes, Bill McLain,

Richard Stone

ALTERNATES-	John Richards, Ken Gerecke

##### October 2004

CREW-		Terry Daeumler, John Richards, Ford Babcock, Bill McLain,

Pete Villanacci

ALTERNATES-	Charles Barnes, Ken Gerecke

##### November 2004

CREW-		Terry Daeumler, John Richards, Charles Barnes, Ken Gerecke,

Bill McLain

ALTERNATES-	Ford Babcock, Pete Villanaci

##### Employee’s Families

| EMPLOYEE | WIFE | CHILDREN |
| --- | --- | --- |
| Ford Babcock | #### Yes | #### No |
| Charles Barnes | #### Yes | #### One |
| Terry Daeumler | #### Yes | #### One |
| Ken Gerecke | #### No | #### No |
| Bill McLain | #### No | #### No |
| John Richards | #### Yes | #### Two |
| Richard Stone | #### No | #### No |
| Pete Villanaci | #### Yes | #### Two |

WEST WATER TREATMENT PLANT

PRE SEASON CHECK LIST

1.	Request volunteers for hurricane crew, develop duty roster and schedule personnel.  All personnel are deemed essential and must be available as directed.

2.	Duty roster at the West Plant will consist of the Lead Operator, E.O.C. short wave radio operator, Instrumentation and Control Tech.), a Utility Maint. Mechanic, and two water plant certified  operators.

3.	Review the previous year's hurricane procedure and update it.

- Check stored emergency supplies using hurricane checklist.

- Check lunchroom hurricane supplies and purchase any needed items.

6.	Fill bulk diesel tank at the beginning of the storm season.

7.	Bulk chemical tanks should be kept as full as possible throughout the hurricane season.

8.	A good stock of spill supplies and other chemicals should be kept during hurricane season.

9.	All batteries for generator and emergency equipment should be checked and replaced if necessary.

WEST WATER TREATMENT PLANT

HURRICANE SEASON SUPPLY LIST

Batteries (AA)			________		Safety Vests 		________

Batteries (AAA)		________		Flash Lights 		________

Batteries (C)			________		Lanterns 		________

Batteries (D)			________		Shovels (round) 	________

Batteries (6 Volt)		________		Shovels (square)	________

Batteries (9 Volt)		________		Axe			________

Duct Tape			________		PVC Cleaner		________

Electrical Tape			________		PVC Glue		________

Masking Tape			________		PVC Pipe & Fittings	________

Jumper Cables			________		Plastic Wire Ties	________

Rope				________		Hammer		________

Rain Suits (small)		________		Hand Saw		________

Rain Suits (medium)		________		Hack Saw		________

Rain Suits (large)		________		Screwdrivers		________

Rain Suits (X large)		________		Pliers (all types)	 ________

Rain Suits (XX large)		________		First Aid Kits		________

Rubber Boots			________		Acetic Acid		________

Work Gloves			________		Citric Acid		________

Rubber Gloves			________		Chlorine		________

Hard Hats			________		Hydrochloric Acid	________

Safety Cones			________		Soda Ash		________

Safety Flags			________		Sodium Hydroxide	________

# HURRICANE CREW SUPPLY LIST

- Clothes for three or four days (include City Uniforms and City I.D.)

- Pillows, sheets and blankets

- Medicine and any special food

- Flashlights, battery operated lighting and/or lantern

- Radio and/or portable television

- Batteries for radios, lighting, etc.

- Toiletries

- Towels and wash cloth

- Non-perishable snacks

- Non-perishable food for several days

- Perishable foods can be brought in

- Laundry soap and cloth washing supplies

- Games, books, etc.

- Eye glasses if needed (back-up pair may be a good idea)

WEST WATER TREATMENT PLANT

HURRICANE WATCH ISSUED

1.	Review hurricane procedure, duty roster, and schedule with staff.

2.	All West Plant vehicles should be refueled at Public Works.

3.	The facility grounds should be inspected and cleaned up.

4.	All empty barrels, concrete blocks, ladders, etc., should be brought inside for safe storage.

5.	Hurricane Crew should be placed on stand-by alert.

HURRICANE WARNING ISSUED

1.	All hurricane crew members will be released to secure their homes and collect some of their belongings such as: pillows, blankets, sleeping bags, clothing and food.

2.	A reporting time for hurricane crew will be given.  At that time non-hurricane personnel will be issued portable radios and sent home.

3.	Vehicles will be placed in the garage areas.

4.	All hurricane shutters will be closed.

5.	All gates will be closed.

6.	All hurricane crew members and families will be assigned sleeping quarters and work shifts assigned by the Chief Operator.

7.	H.A.M. radio should be set up and the radio operator should check in with E.O.C.

8.	Ground storage tank at West Plant should be filled as much as possible.

9.	All V.F.D. breakers for the high service pumps be shut off.  Use pumps two (2) and five (5).

10.	The generator control should be changed from AUTO to OFF to save fuel and protect it from the blowing rain.

11.	Flashlights and lanterns should be issued to the hurricane crew and families.

12.	Weather information should be monitored by the control room operator using the TV in control room, the computer internet and the weather band radio.

13.	All chemical day tanks should be filled and used during the storm.

HURRICANE WARNING ISSUED (CONTINUED)

- All valves at the bulk tanks should be shut off to prevent draining if the pipes are damaged or broken.

- The West Plant will run as long as possible using Florida Power & Light.

DURING THE HURRICANE

1.	One operator will be monitoring the West Plant Control Room.

2.	One operator will be on second man status to assist the operator when needed.

- One operator will get some sleep and relieve the control room operator at the end of their shift.  That operator becomes the second person.

- When Florida Power and Light is lost, all computers will be shut off to save the uninterrupted power supply (UPS).

- Back up lighting should be used for the remainder of the storm.

POST HURRICANE

1.	The West Plant facility, equipment, chemical tanks, etc., will be inspected by hurricane crew.

2.	If the central communications tower is disabled, all portable radios should be switched to Channel K.

3.	Hurricane Crew will make any repairs needed to equipment (if possible) to prepare plant for start up.

4.	Chief Operator will report to the West Plant and check with the Utilities Director or Deputy Director for status of the East Plant, Wells, Ground Storage Tanks and Distribution System.

5.	A decision will then be made when to restart the West Water Plant.

6.	If the West Plant will be started, the generator should be put back on Auto.

7.	The clearwell, degassifiers and off-gas scrubber can be by-passed if needed.

8.	A decision will be made on what type of chlorine residual will be used (free or combined) for start-up of the plant.

9.	The East and West Water Plants, if on generators, will alternate to save fuel.

- All other staff will be called in as needed.

11.	Crews will remove debris from the facility.

12.	Staff will be utilized as needed and assigned by the Fire Chief, Utilities Director, City Manager or the Deputy Director, depending on City’s needs.

- The emergency telephone line will be transferred to the Emergency Operation Center (EOC) to handle all calls while the operator runs the treatment plant.

14.	The Chief Operator will submit a detail report of events, conditions, damage assessment, personnel hours worked, materials used, etc., to the Utility Director within 24 hours after the storm.

OPERATIONS PERSONNEL (WEST)

NAME			VEHICLE	HOME PHONE		Cell Phone	TITLE

David Ailstock		     102		433-8779		601-9908	Chief Operator

Ford Babcock		     102		434-5608		676-3197	Water Process Tech

Charles Barnes		     102		733-9219				Operator I

Terry Daeumler		     102		737-1138		523-7327	Operator III

Alen Galloway		     102		439-0142				Water Process Tech.

Ken Gerecke		     137		582-4039		389-6546	Maint. Mechanic

James (	Bo) Mathis	     102		731-1745				Water Operator I

Robert Mulay		    102		740-1975		436-2841	Water Process Tech

Leonard Allen		    107		737-1651		524-0557	Water Process Tech.

John Richards		    102		969-1100		714-9691	Operator II

Michael Rosenberg	    102		433-1062				Operator III

Richard Stone	               137		736-8740		551-0714 	Maint. Mechanic

Bill McLain		  1102		533-7494		602-4408	Inst. & Control Tech

Pete Villanaci		  137		585-6229				Maint. Mechanic

Thornale Johnson	  137		369-2542				Water Process Tech

Gus Gall		   137					628-7805	Utility Painter

WATER QUALITY DIVISION

Steve Evans				499-1533		523-8590	Supervisor

Gary Ezzell			    	967-3652				Chemist

Arsenio Elizondo			686-0237				Lab Tech Sr.

Liz Meeker		1104		547-9814		523-8589	Lab Technician

Mark Phillips		163		965-8231		523-4047	Lab Field Technician

Gloria Borges				784-8054				Lab Tech Sr.

CHEMICAL SUPPLY

CHEMICAL		SUPPLIER 		TELEPHONE		CONTACT PERSON

Ammonia		Bower Ammonia	1-800-643-6226		Mark Ferreira

Acetic Acid		Univar			813-677-8414		Sales Representative

Bi-Sulfate		Univar			813-677-8414		Sales Representative

Chlorine		Jones Chemical		1-888-293-8321		Sales Representative

Citric Acid		Univar			813-677-8414		Sales Representative

Diesel Fuel		B.V. Oil		1-800-586-2862		Sales Representative

EDTA			Univar			813-677-8414		Sales Representative

Hydrated Lime		Univar			813-677-8414		Sales Representative

Hydrochloric Acid	Univar			813-677-8414		Sales Representative

Phosphate		Shannon Chemical	1-610-363-9090		Dan Flynn

Sodium hydroxide	Jones Chemical		1-888-293-8321		Sales Representative

Sod. Laurel Sulfate	Univar			813-677-8414		Sales Representative

Sulfuric Acid		Satco			800-633-1358		Pat Dewitt

Fluoride		Allied Universal	800-542-2672		Sales Rep

ELECTRICAL REPAIR AND SUPPLIERS

Company			Telephone		Contact Person

Advanced Generator		561-798-4280		Rich Cordis

Energy Efficient		561-832-2881		Bill Scott

Florida Power and Light		561-832-2881		Sherri Alan

Gilmore Electric		561-832-2881		Bill		Repair

##### PART VENDORS

Company			Telephone		Parts			Contact

A-1 Industrial			561-588-0802		Steel & Aluminum	Sales Representative

Adelphia			561-967-8405		Cable TV		Sales Representative

AGM Electronics		520-722-1000	I	Instrumentation		Missy

Air Compressor Works		561-844-4559		Air Compressor		Bill Carley

All Keyed Up			561-364-4255		Doors & Locks		Tim Hill

AMJ Equipment Corp		800-881-1487		ProMinet Pumps	Mike Parnell

Anixter Brothers Inc.		561-997-0838		EDCO Protection	Sandy Ray

Baker Petrolite (Cronox)	800-531-2025		Annulus Chemical	Sales Representative

Boynton Pump Supply		561-732-9810		Plumbing Parts		Sales Representative

Broward Pump Supply		561-732-2424		Plumbing Parts		Sales Representative

Carlin,Green & Associates	813-622-7738		Keystone Valves	Jeff Hegedus

CH2M Hill			561-737-6665		Engineering Services	Tom McCormack

Classic Controls		561-641-3017		JYC Instruments	Rafael Lemus

Code Line			800-289-2766		Membrane Vessels	Bob Pallais

Control System Design		941-755-2454		Computer Programming	Mark Biehl

Condo Electric			305-691-5400		Motors Rewinds	Muhamud

Consolidated Electric		561-276-0362		Electric Parts		Sales Representative

Crom				800-289-2766		Ground Storage Tank	Jim Neff

Cutler Hammer			954-571-8282		VFD Drives		Cryette

Data Flow Systems		407-259-5009		Well Control System	Tom & Damien

Delray Fire Extinguishers	561-278-1094		Fire Extinguishers	Sales Representative

Diller Brown			561-851-7830		Auma Valves		Etta Daggett

Diversified Well Drilling	813-988-1132		Injection Well		Mack or Jack

Farmer & Irwin			561-842-5316		Air Conditioning	Jim Whitty

Ferguson Underground		561-737-2250		Chemtrol Valves	Frank Nagle

Filmtec				561-626-6616		Membranes		Stuart McCellen

Fisher Scientific		800-766-7000		Lab Chemicals		Sales Representative

Florida Bolt			561-842-2658		Nuts & Bolts		Kirk Butler

Four Steel			561-734-1100		Steel & Aluminum	Sales Representative

G.K. Pressure Cleaning		561-734-1253		Pressure Cleaning	Gary Kimberly

Grainger			561-684-6895		Parts & Supplies	Jim Cook

Graybar Electric		561-585-6148		Electrical Part		Sales Representative

H.C. Warner			772-288-0599		Cartridge Filters	Gil Turner

H.S. White			954-566-3900		Hoses			Sales Representative

Hudson Pumps			863-665-7867		Goulds Pumps		Nate Geiger

Jacobs Group			813-854-5297		Pulsa Feeder		Paul Jacobs

Liquid Air			561-842-2288		Lab Gab		Sales Representative

Masthead			800-645-5476		Hoses			Cesar Figueroa

Atlantic Filter			561-683-0101		Softeners		Jim Wakem

Millipore			800-645-5476		SDI Parts		Sales Representative

Nolan Tropical Plumbing	561-278-6855		Plumbing Parts		Sales Representative

Overhead Door			561-428-1480		Storm Shutters		Jim Jeschonek

Perm Alert ESP			615-444-4910		Cont. Alarm System	Randy Teat

Productive Alternative		218-736-5668		Rain Gauge		Sales Representative

Reliance Electric		813-289-0635		Motor Drives		Marion Alexander

Ritz Safety			800-451-3077		Safety Products		Sales Representative

Robicon			724-339-9501		VFD Drives		Eric Woodside

Thyssen Miami Elevator	561-842-5761		Elevator Service	Mike Martelli

Siemens Energy & Automation	954-428-7258		Texas Instruments	Richard Winkler

Solares				561-219-9620		Ashcoft Gauges		Andy Foster

Systems Components		352-237-8848		Bulk Tank Dryers	Phyllis Maxey

Wallace & Tiernan		800-727-8798		Chlorinators, Etc.	Sales Representative